TDNK Chiller

Technical Manual

Please read the in manual carefully before installing the controller! All rights reserved. Any reproduction of the manual will be prosecuted.

Table of contents

1 Instructions	1

2 Specifications	1

3 Panel Diagram	1

4 First Power-on	1

5 Common Screens	2

5.1 Main Screen	2

5.2 Alarm Screen	2

6 Common Operation	2

6.1 Quick Modification of Setting Temperature	2

6.2 Query/Reset Fault	2

7 Function Menu	3

8 Parameter Operation	4

9 User Parameters Table	4

10 Manufacturer Menu	5

10.1 Procedures of Entering Manufacturer Menu	5

10.2 Details of Manufacturer Menu	5

10.3 Manufacturer Debugging	5

10.4 Configuration Guide	6

11 Fault List	7

12 Control	10

12.1 Logic of compressor	10

12.2 Logic of pump freeze protection	10

13 Manufacturer Parameters Table	10

14 Standard Series Air-cooled Chiller Specifications Table	14

15 Instructions for machine parts and Electrical Diagram	15

# 1 Instructions

Dear Customer:

Thank you for choosing PUNP products!

For your convenience, please read the instructions carefully and follow the steps of the Manual.

# 2 Specifications

| No. | Specification Parameter | Description |  | No. | Specification Parameter | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Rated input voltage | 220-250VAC 50/60HZ |  | 6 | Switch Output | 5 relays 250VAC 2A |
| 2 | Temperature Range | -40~212℉ |  | 7 | Relay load type | D01:annunciator D02-D05: contactor or valve |
| 3 | Measurement Accuracy | 32.18℉@77℉ |  | 8 | Switch Input | 12 passive signal inputs |
| 4 | Working Environment | 14℉~140℉,≤85%RH non-condensation |  | 9 | Analog Input | 1 NTC temperature sensor |
| 5 | Storage Environment | -4℉~158℉,≤85%RH non-condensation |  | 10 | Current Input | 4 ways of current (0.3~35A) |

# 3 Panel Diagram

# 4 First Power-on

The controller needs to be configured when powered on for the first time. Please refer to 10.4 Configuration guide for specific operation.

# 5 Common Screens

Commonly used screens include the main screen and the alarm screen.

| 5.1 Main Screen | 5.2 Alarm Screen |
| --- | --- |
| The system will enter the main screen after countdown, which displays as follows: Press + for 3 seconds on the main screen can change the language quickly. | In case of unit failure, the alarm screen is as follows: Press + during down count and enter Language screen, press or to change current Language, press to quit without saving, press to save and quit. |

# 6 Common Operation

6.1 Quick Modification of Setting Temperature

If the user parameter [Lock T.set] is set to "No", the setting temperature can be modified directly in the main screen, with operation details as follows: Note: the setting temperature can also be modified in the user parameters.

6.2 Query/Reset Fault

In case of fault, the alarm screen will automatically pop up. The operation details of query and reset faults are as follows: 7 Function Menu Press the button on the main screen to enter the Function Menu, which includes five items as the table below: No. Menu Item Funtion Remark 1 User Settings To display user parameters For number of user parameters and their implications, please refer to: 9 User Parameters Table. 2 Unit Status To display the current operating status of the unit Current value is not displayed when current module is not used. 3 History List Allowing the query of the last 10 faults Press for 2s to clear the fault history. 4 Comp run time To display the cumulative operation time of the compressor 5 Version To check the current software version

# 8 Parameter Operation

For the modification operation of parameter value, the user’s modification of setting temperature will be described as an example.

# 9 User Parameters Table

The implication of each parameter in the user parameters is listed in the following table:

| No. | Parameter Name | Factory Default | Setting Range | Remark |
| --- | --- | --- | --- | --- |
| 1 | Lock T.set | No | Yes ~ No | Yes: the set temperature can not be modified on the main screen when locked. No: the set temperature can be modified on the main screen. |
| 2 | T.setpoint | 12.0℃ | [T.setpoint min] ~[ T.setpoint max] | Setting range is limited by the manufacturer parameters [T.setpoint max], [T.setpoint min]. (When the [TEMP Unit] is set “Fahrenheit”, the parameter is not displayed.) |
| 3 | T.setpoint | 53.6 ℉ | [T.setpoint min] ~[ T.setpoint max] | Setting range is limited by the manufacturer parameters [T.setpoint max], [T.setpoint min]. (When the [TEMP Unit] is set “Celsius”, the parameter is not displayed.) |
| 4 | TEMP Unit | Celsius | Celsius；Fahrenheit |  |
| 5 | Contrast | 32 | 20~44 | Adjust the LCD contrast |
| 6 | On/Off type | Local | Local / Local + Remote / Remote | Local: the unit can only start and stop locally. Local + Remote: the start and stop of the unit can be controlled both locally and remotely. Remote: the unit can only start and stop remotely. |
| 7 | Backlight On | 0 | 0~255 minute(s) | 0: backlight is not turned off. |
| 8 | Language | chinese | chinese~English | Select the display language. |
| 9 | Comp Select | Two Comp | 1#Comp/2#Comp/Two Comp | Select the Comp to run. if select one comp the other does not work. The parameter is not listed for the single comp machine. |

# 10 Manufacturer Menu

Press + in the main screen to enter the Enter Password screen and enter the correct manufacturer password (default 4561, which is recommended to change). Then enter the Manufacturer Function Menu, which includes five items.

## 10.1 Procedures of Entering Manufacturer Menu

## 10.2 Details of Manufacturer Menu

The details and function of manufacturer menu are shown in the following table:

| No. | Parameter Item | Function | Remark s |
| --- | --- | --- | --- |
| 1 | Manuf. setting | To set the parameters commonly used by the manufacturer | Refer to 13 Manufacture Parameters for specific parameters. |
| 2 | Manuf. debug | To debug the abnormal operation of each electrical part of the unit | Not available during the unit operation. |
| 3 | Config guide | Commonly used parameters of config the unit | Not available during the unit operation. The screen will pop up when powered on for the first time. |
| 4 | Initialize | For initialize all parameters of the machine. | Refer to 10.5 Manufacture Parameters for the initial values of the parameters. |
| 5 | Password Set | To set the password to enter manufacturer menu. | The default value is 4561, which is recommended to change. |

Note: Press + in the manufacturer menu for 2 seconds can reset the accumulative operation time of the compressor.

## 10.3 Manufacturer Debugging

Manufacturer debugging is mainly used to test whether the operation of each electrical part of the unit is normal, which is not available when the unit is under operation.

Method: to determine whether the unit is normal by testing three-phase power input, seven alarm inputs (10 alarm inputs for two compressors) and 5 relay outputs. For alarm input, it only displays the test result. If the result is normal the wiring is good and parameter settings are correct; if it alarms, with flashing display of alarm characters, then make sure whether the external wiring is good and the parameter settings are consistent.

## 10.4 Configuration Guide

Configure the common parameters of the machine. For the number of parameters of configuration guide and the significance, please refer to 13 Manufacturer Parameters Table. Access is not available during the unit operation.

Refer to the Parameter Operation for specific configuration method. The Configuration guide screen will pop up when powered on for the first time. And if you click “Cancel” operation without configuring at this point, the Configuration guide screen will still pop up when powered on next time. Once you have entered the Configuration guide, the Configuration guide screen will not pop up when powered on and you can only enter the Configuration guide through the Manufacturer Menu.

# 11 Fault List

| Fault | Description | Test Conditions | Troubleshooting | Solution |
| --- | --- | --- | --- | --- |
| 1#Comp.P high | High pressure of compressor1 | Test when the compressor button has pressed | Stop compressor1 only without affect other equipments to work. [Note1] | Check if the input is consistent with the switch setting. |
| 1#Comp.P low | Low pressure of compressor1 | If the [LP detect dly] is 0, test when the compressor button has pressed; If the [LP detect dly] is not 0, then compressor1 runs the test. |  |  |
| 1#Comp overload | The compressor1 overload | Compressor1 runs the test. |  | Check if the input is consistent with the switch setting. |
| 1#Comp.I high | The current of compressor1 is too high |  |  | Check if the rated current of compressor1 is input is reasonable. |
| 1#Comp.I low | The current of compressor1 is too low |  |  | Check if the measure tool of the compressor1 current is connect. |
| 1#T.Vent high | The vent temperature of compressor1 is too high |  |  | Check if the input is consistent with the switch setting. |
| 2#Comp.P high | High pressure of compressor2 | Test when the compressor button has pressed | Stop compressor2 only without affect other equipments to work. [Note2] | Check if the input is consistent with the switch setting. |
| 2#Comp.P low | Low pressure of compressor2 | If the [LP detect dly] is 0, test when the compressor button has pressed; If the [LP detect dly] is not 0, then compressor2 runs the test. |  |  |
| 2#Comp overload | The compressor2 overload | Compressor2 runs the test. |  | Check if the input is consistent with the switch setting. |
| 2#Comp.I high | The current of compressor2 is too high |  |  | Check if the rated current of compressor2 is input is reasonable. |
| 2#Comp.I low | The current of compressor2 is too low |  |  | Check if the measure tool of the compressor2 current is connect. |
| 2#T.Vent high | The vent temperature of compressor2 is too high |  |  | Check if the input is consistent with the switch setting. |
| Temp.low AL | The liquid temperature is too low | Test after cold pump starts | Stop the compressor and delay to stop the cool pump, and do not stop the cold pump. | Check if the Liquid temperature is lower than the set temperature of Liquid protection. |
| T.high warn | The liquid temperature is higher than the warn value. |  | Alarm only without affect other equipments to work. | Check if the Liquid temperature is higher than the set temperature of Liquid warn. |
| Temp.high AL | The liquid temperature is too high |  | If the [Temp.high AL] is set “Pump keep”,Stop the compressor and delay to stop the cool pump, and do not stop the cold pump; If the [Temp.high AL] is set “Pump stop”, Stop the unit in case of fault. | Check if the Liquid temperature is higher than the set temperature of Liquid protection. |
| Anti-freez.AL | Antifreeze alarm | Power on to test | Stop all the compressor and cool pump, and do not stop the cold pump. | Check if the antifreeze input is consistent with the switch setting. |
| Probe break | The liquid temperature sensor is break |  |  | Check if the temperature probe is in proper contact. |
| Probe short | The liquid temperature sensor is short |  |  |  |
| cool fan overld [Note3] | The cool pump or fan overload | Test after Cool pump starts | Stop compressor1 and cool pump or fan only | Check if the fan1 overload input is consistent with the switch setting. |
| Cool.I high AL | The current of cool pump or Fan is too high |  |  | Check if the rated current of cool is input is reasonable. |
| Cool.I low AL | The current of cool pump or Fan is too low |  |  | Check if the measure tool of the cool current is connect. |
| Cool W.flow AL | Lack of cool water flow | Test after the cool pump starts for [Cool on delay] time | Stop compressor1 and cool pump or fan only | Check if the cool water flow input is consistent with the switch setting. |
| Cold W.flow AL | Lack of cold water flow | Test after the cold pump starts for [Pump on delay] time | If the [Lack of water] is set “Pump keep”, Stop compressor and cool pump in case of fault. If the [Lack of water] is set “Pump stop”, Stop the unit in case of fault. | Check if the cold water flow input is consistent with the switch setting. |
| Cold Pump Overld [Note3] | The cold pump overload | Test after cold pump starts | Stop the unit | Check if the cold pump overload input is consistent with the switch setting. |
| Pump.I high AL | The current of cold pump is too high |  |  | Check if the rated current of cold is input is reasonable. |
| Pump.I low AL | The current of cold pump is too low |  |  | Check if the measure tool of the cold current is connect. |
| Phase AL | The three-phase power input is alarm | Power on to test | Stop the unit | Check if there is default phase or anti-phase in the three-phase power input and if the switch is correct. |
| Water lv. AL | The water level is low | Power on to test | If the [Low water lv.] is set “Pump keep”, Stop compressor and cool pump in case of fault. If the [Low water lv.] is set “Pump stop”, Stop the unit in case of fault. | Check if the water level input is consistent with the switch setting. |
| Need Maintain | The total time of compressor run over the allow value | Test after cold pump starts | The unit cannot start once stops (the accumulative operation time of compressor exceeds the set value). |
| 1#Comp Oil Low | The comp oil level is low | Compressor1 runs the test. | Stop the compressor and delay to stop the cool pump, and do not stop the cold pump. | Check if the comp oil level input is consistent with the switch setting. |
| 2#Comp Oil Low |  |  |  |  |

[Note 1]: In case of "1#Comp.P low " fault, if [LP stop pump] is not zero, the troubleshooting program is: to immediately stop all compressors and cool pump, delay the [LP stop pump] and stop the cold pump. If [LP stop pump] is zero, then the troubleshooting program is: to only stop compressor1 without affect other equipments to work.

[Note 2]: In case of "2#Comp.P low " fault, if [LP stop pump] is not zero, the troubleshooting program is: to immediately stop all compressors and cool pump, delay the [LP stop pump] and stop the cold pump. If [LP stop pump] is zero, then the troubleshooting program is: to only stop compressor2 without affect other equipments to work.

[Note3]:

| [Machine type] | the screen real display when Cold Pump overload | the screen real display when Cool Pump overload |
| --- | --- | --- |
| AIR-WATER | Cold Pump Overld | Cool Fan Overld |
| W-W SYS. | Cold Pump Overld | Cool Pump Overld |
| AIR-AIR | Cold Fan Overld | Cool Fan Overld |
| WATER-AIR | Cold Fan Overld | Cool Pump Overld |

# 12 Control

## 12.1 Logic of compressor

Double compressor but select only one / Single compressor:

The heating process, the compressor ON when PV ≥SV + ADD.

The cooling process, the compressor OFF when PV < SV – SUB

Double compressors:

a) If [Unload offset] is not 0

The heating process, one compressor ON when PV> SV and two compressors ON when PV≥ SV + ADD.

The cooling process, if two compressors ON currently, one compressor OFF when PV < SV and two compressors OFF when PV < SV - SUB.If compressor ON currently, the compressor OFF when PV <SV-SUB.

b) If [Unload offset] is 0

The heating process, one compressor ON when PV> = SV + ADD; after the time of [Capacity ctrl], if PV≥ SV + ADD remains, two compressors ON.

The cooling process, the compressor OFF when PV <SV.

Note:   PV: The liquid temperature            SV: set temperature

ADD: load temperature diefference     SUB: unload temperature difference

## 12.2 Logic of pump freeze protection

a) When [T.freeze prot] = “forbid”, there is no pump freeze protection.

b) Otherwise under the idle state:

if SV ≤ [T.freeze prot], the pump opens;

if SV ≥ [T.freeze prot] + 2, the pump will close after 10 seconds.

# 13 Manufacturer Parameters Table

Parameters set by the manufacturer and parameter meanings are listed as follows: ("*" is for parameters of the configuration guide)

| Setting Item | Name of Parameter | Factory Default | Setting Range | Remark |
| --- | --- | --- | --- | --- |
| Func. Setting | *One-Key start | Forbid | Forbid ~ Use | Forbid: the compressor is allowed to ON only when press the compressor button; Used: the compressor allows ON when press the pump button. |
|  | Auto start up | Forbid | Forbid ~ Use | Use: the unit starts automatically when powered on; Forbid: the unit doesn’t start automatically when powered on; When the user parameter [On/Off type] is set to be"Remote", the electrical autostart is invalid. |
|  | Alarm output | Keep when mute | Keep when mute; Stop when mute | Keep when mute: press the “alarm output” parameter to take action once a fault occurs; Stop when mute: press the “alarm output” parameter to take action in case of no fault after silencing. |
|  | Alarm type | N.O | N.O~N.C | N.O: the alarm relay is ON in case of faults; N.C: the alarm relay is OFF in case of faults. |
|  | *DI5 function | Water switch | Water switch; Vent1 temp | Water switch: DI5 input for water level detection Vent1 temp: DI5 input for Vent1 temperature detection |
|  | *DI9 function | Phase swtich | Phase swtich; Cool W.flow Vent2 temp; 2#Comp Oil LVL | Phase swtich: DI9 input for phase sequence detection Cool W.flow: DI9 input for cool water flow detection Vent2 temp: DI9 input for Vent2 temperature detection 2#Comp Oil LVL: DI9 input for 2#comp oil level detection |
|  | *Low water lv. | Pump stop | Pump stop ~ Pump keep | Pump stop: stop the cold pump in case of low water level fault; Pump keep: do not stop the cold pump in case of low water level fault. |
|  | *Lack of water | Pump stop | Pump stop ~ Pump keep | Pump stop: stop the cold pump in case of cold water flow fault; Pump keep: do not stop the cold pump in case of cold water flow fault. |
|  | *Current detect | Use | Forbid ~ Use | Use: there is a current detection module; Forbid: no current detection module |
|  | *1#Comp.I rating | 0.3A | 0~35.0A | 0A: do not detect the current fault. When [Current detect] is set “Forbid”, those parameter is not displayed. (if the rating current of Comp or Pump is lower 1A, when using please winding two or three laps on the sensor) |
|  | *2#Comp.I rating | 0.3A | 0~35.0A |  |
|  | *Pump. I rating | 0.3A | 0~35.0A |  |
|  | *Cool. I rating | 0.3A | 0~35.0A |  |
|  | *Phase monitor | On_board | On_board; Forbid; IO_input | Onboard: use the controller’s own three-phase power protection; Switch input: use an external three-phase power protection. (The external three-phase power protection can only be ued when [DI9 fuction] is set " Phase swtich" .) Forbid: do not use three-phase power detection function. |
|  | DI1 input opt | Cool overload | Cool overload; Anti-freezing | Selection of switch DI1 input function |
|  | *Comp number | 2 | 1~2 | Selection of the number of compressor |
|  | *Machine type | AIR-WATER | AIR-WATER; W-W SYS.; AIR-AIR; WATER-AIR | AIR-WATER. fan-cooled water chiller, W-W SYS. :water-cooled water chiller, AIR-AIR : fan-cooled fan cooler WATER-AIR : water-cooled fan cooler |
|  | *Lang switch | Use | Forbid ~ Use | Use: Allows users to switch between English and Chinese. Forbid: Forbid users to switch between English and Chinese. |
|  | *Temp.high AL | Pump keep | Pump stop ~ Pump keep | Pump stop: stop the cold pump in case of Temp.high fault; Pump keep: do not stop the cold pump in case of Temp.high fault. |
|  | *DI2 function | Remote | Remote; 1#Comp Oil LVL | Remote:DI2 input for remote switch 1#Comp Oil LVL: DI2 input for 1#comp oil level detection |
|  | *DO1 function | Alarm signal | Alarm signal; Run signal | If [DO1 fuction] is “Alarm signal” [Alarm type] is N.O: the alarm relay is ON in case of faults; [Alarm type] is N.C: the alarm relay is OFF in case of faults. If [DO1 fuction] is “Run signal” [Alarm type] is N.O: the alarm relay is OFF when the unit is normal running; [Alarm type] is N.C: the alarm relay is ON when the unit is normal running. |
| Temp. Setting | Load offset | 1.8℉ | 0~18.0℉ | Temperature deviation of load the compressor |
|  |  |  |  | Fahrenheit ℉ |
|  | Unload offset | 1.8℉ | 0~18.0℉ | Temperature deviation of unload the compressor |
|  |  |  |  | Fahrenheit ℉ |
|  | T.setpoint max | 86.0℉ | -36.4~211.8℉ | To limit the temperature of user set. |
|  | T.setpoint min | 41.0℉ | -36.4~211.8℉ | Fahrenheit ℉ |
|  | T.bias | 32℉ | -49.82～49.82℉ | Compensation for the liquid temperature |
|  |  |  |  | Fahrenheit ℉ |
|  | T.low protect | 39.2℉ | -40.0~211.8℉ | Fault of “Temp.low AL” warning is reported when the liquid temperature is lower than the set value. |
|  |  |  |  | Fahrenheit ℉ |
|  | T.high warn | 122.0℉ | 32.0~211.8℉ | Fault of “Temp.high warn” warning is reported when the liquid temperature is higher than the set value. |
|  |  |  |  | Fahrenheit ℉ |
|  | T.high alarm | 140.0℉ | 32.0~211.8℉ | Fault of “Temp.high AL” warning is reported when the liquid temperature is higher than the set value. And Stop the compressor and delay to stop the cool pump. |
|  |  |  |  | Fahrenheit ℉ |
|  | T.high reset | 9.0℉ | 0~179.8℉ | If liquid temperature<[T.high alarm]–[T.high reset], manual reset of “Temp.high AL” fault is allowed; If liquid temperature<[T.high warn]–[T.high rese], the “Temp.high warn” fault is automatically reset; |
|  |  |  |  | Fahrenheit ℉ |
|  | T.freeze prot | forbid | forbid~59.0℉ | No such function when set to forbid. |
|  |  |  |  | No such function when set to forbid(32.0℉). |
| Time Setting | Pump on delay | 10 S | 1~255 S | Delay after cold pump startup. |
|  | Cool on delay | 10 S | 1~255 S | Delay after cool pump startup. |
|  | Capacity ctrl. | 5 S | 0~255 S | Control the compressor ON/OFF every [Capacity ctrl.] interval time; For double-compressor control, if the conditions of two compressors ON are satisfied, then one of the compressors ON and the other after the time of [Capacity ctrl.]. |
|  | Comp protect | 60 S | 0~255 S | To avoid frequent ON/OFF the compressor, the interval between the start of two compressors must be greater than the set value. |
|  | Input stable | 2 S | 0~255 S | The time General fault stable. |
|  | W.flow stab. | 5 S | 0~255 S | It is considered to be valid only when the water flow alarm continue for the time. |
|  | LP detect dly | 60 S | 0~255 S | Compressor low-pressure fault input is allowed only when the compressor has run for the set time. |
|  | LP stable | 5 S | 0~255 S | Low-pressure fault stable time |
|  | LP stop pump | 0 S | 0~300 S | 0: the parameter has no effect . Non-0: in case of low pressure fault of the compressor, immediately stop all compressors and cool pump, delay the [LP stop pump] and stop the cold pump. |
|  | Comp operation | 0 H | 0~9999 H | 0: this parameter has no effect. Non-0: the compressor cannot start when the accumulative operation time is greater than the set value. |
|  | Comp shift | 0 Min | 0~255 H | 0: the parameter has no effect ; Non-0: a compressor will automatically switch to another after it has run continuously for that time. |
|  | 1#Comp.I avoid | 2 S | 1~255 S | The current fault of 1#compressor can only be detected after 1# compressor has started for the set time. (When the [Current detect] is set “forbid”, the parameter is not displayed.) |
|  | 2#Comp.I avoid | 2 S | 1~255 S | The current fault of 2#compressor can only be detected after 2# compressor has started for the set time. (When the [Current detect] is set “forbid”, the parameter is not displayed.) |
|  | Pump. I avoid | 2 S | 1~255 S | The current fault of cold pump can only be detected after it has started for the set time. (When the [Current detect] is set “forbid”, the parameter is not displayed.) |
|  | Cool. I avoid | 2 S | 1~255 S | The current fault of cool pump can only be detected after it has started for the set time. (When the [Current detect] is set “forbid”, the parameter is not displayed.) |
|  | Comp Oil dly | 5 S | 1~255 S | 1#Comp/2#comp oil low stable time |
| Input Setting | *Freez overload | N.O | N.O ~ N.C | Selection of switch input mode N.O: switch off with no fault; N.C: the switch is closed with no fault. |
|  | *Cold W.flow | N.C | N.O ~ N.C |  |
|  | *W.level switch | N.C | N.O ~ N.C | When [DI5 fuction] is " Vent1 temp", it is the place for N.O and N.C settings of vent1 temperature detection. |
|  | *Comp overload | N.O | N.O ~ N.C | Selection of switch input mode N.O: switch off with no fault; N.C: the switch is closed with no fault. |
|  | *Low pressure | N.C | N.O ~ N.C |  |
|  | *High pressure | N.O | N.O ~ N.C |  |
|  | *Phase error | N.O | N.O ~ N.C | When [DI9 fuction] is " Cool W.flow", it is the place for N.O and N.C settings of cool water flow switch. When [DI9 fuction] is "Vent1 temperature", it is the place for N.O and N.C settings of vent1 temperature detection. |
|  | *Cool overload | N.C | N.O ~ N.C | When [DI1 input opt] is " Anti-freezing", it is the place for N.O and N.C settings of antifreezing switch. |
|  | Comp Oil switch | N.C | N.O ~ N.C | 1#Comp/2#comp oil low N.O: switch off with no fault; N.C: the switch is closed with no fault. |
|  | *Temp Low Reset | Manual Reset | Manual Reset; Auto Reset; | Reset type of “Temp.low AL” |

[Note]: remote switch, if the remote control is used, the unit will start up when remote switch input is closed and stop when remote switch input is disconnected.

# 14.Standard Series Air-cooled Chiller Specifications Table

| Parameter | Model | SJ-05AS46 | SJ-05AS22 | SJ-10AD46 | SJ-10AD22 | SJ-15AS46 |
| --- | --- | --- | --- | --- | --- | --- |
| Coling Capacity | KW | 14.5 | 14.5 | 29 | 29 | 44.5 |
|  | BTU/h | 45560 | 45560 | 99760 | 99760 | 153080 |
| Motor Input | KW | 4.97 | 4.97 | 11 | 11 | 15.5 |
|  | PH | 6.6 | 6.6 | 14.6 | 14.6 | 20.6 |
| Power Supply |  | 3Φ460V 60Hz | 3Φ220V 60Hz | 3Φ460V 60Hz | 3Φ220V 60Hz | 3Φ460V 60Hz |
| Refrigerant | Name | R 410A | R 410A | R 410A | R 410A | R 410A |
| Compressor | Control type | Hermetic Scroll |
|  | Motor | KW | 4.22 | 4.22 | 4.22*2 | 4.22*2 | 8.2+4.22 |
| Air Flow | m³/H | 5000 | 5000 | 10000 | 10000 | 15000 |
|  | Scfm | 176575 | 176575 | 353150 | 353150 | 529725 |
| Temp Range | F | 41—104°F | 41—104°F | 41—104°F | 41—104°F | 41—104°F |
| Chilled water | Flow | L/Min | 40 | 40 | 80 | 80 | 125 |
|  |  | GPM | 10.5 | 10.5 | 21 | 21 | 33 |
|  | Tank | Lit | 65 | 65 | 148 | 148 | 264 |
|  |  | GaL | 17 | 17 | 39 | 39 | 69 |
|  | In/out Pipe size | G1" | G1" | G2" | G2" | G2" |
| Water Pump | motor | KW | 0.75 | 0.75 | 1.5 | 1.5 | 1.5 |
|  | pressure | Kpa | 290 | 290 | 205 | 205 | 205 |
|  |  | PSI | 42 | 42 | 29 | 29 | 29 |
| Dimensions | Length | MM | 1070 | 1070 | 1480 | 1480 | 1725 |
|  | Width | MM | 615 | 615 | 710 | 710 | 890 |
|  | Height | MM | 1360 | 1360 | 1530 | 1530 | 1790 |
|  | Length | Inch | 45 | 45 | 58 | 58 | 68 |
|  | Width | Inch | 24 | 24 | 28 | 28 | 35 |
|  | Height | Inch | 53 | 53 | 60 | 60 | 71 |
| Weight | KG | 208.5 | 208.5 | 356 | 356 | 531 |
|  | LB | 459 | 459 | 784 | 784 | 1170 |

# 15：Instructions for machine parts

Model: SJ-05AS46； SJ-05AS22

Electrical Diagram:

Note: the power of the model specifications in accordance with the name plate

Model: SJ-05AS46, SJ-05AS22

Instructions for machine parts

Model:

SJ-10AD46

SJ-10AD22

SJ-15AS46

Electrical Diagram:

Note: the power of the model specifications in accordance with the name plate

Model:

SJ-10AD46

SJ-10AD22

SJ-15AS46